## ELECTRICAL
PROPOSED INTERIOR WORK FOR RENOVATION OF KHARDAH BRANCH INDIAN BANK
UNDER ZONAL OFFICE-BARASAT
II. SCHEDULE OF QUANTITES FOR ELECTRICAL WIRING & LIGHT FAN FIXTURES WORK
ITEM | DESCRIPTION | QNTY. | UNIT | RATE | AMOUNT
NO. |  |  |  | RS. P. | RS. P.
1 | SWITCH/ MCB
Supply & erection of 415V/230V equipment individually on wall housed in MS enclosure with metal front cover for the following:
A | 100A FP SFU with HRC fuse links as main incomer with cable entry box. | 1 | Each |  | 0
B | 40A rated 4P On-Load CO Switch to be connected after the TPN Busbar
| with cable entry box at both ends. | 1 | Each |  | 0
C | 32A TPN SFU with rewirable fuse links for Generator supply. | 1 | Each |  | 0
D | 25A DP MCB for UPS incomer & outgoing. | 4 | Each |  | 0
E | TPN Busbar chamber having 4 nos. 25x6mm CU Bars fixed on insulators. | 1 | Each |  | 0
F | 40A DP RCCB (MAKE :LEGRAND/L&T) | 1 | Each |  | 0
G | 32A 20KA 230-400V, 50/60 HZ FP SURGE PROTECTION DEVICE (HAGER MAKE) | 1 | SET |  | 0
2 | DISTRIBUTION BOARD
Supply & erection of 415V, TPN wall mounting DB housed in Horizontal Double door DB box consisting of the following:-
A | MDB:
i) Incomer- 1 No - 63A 4P MCB (10KA).
ii) Outgoing- 7 Nos. - 32 SP MCB (10KA).
| (UPS supply for Bank, and LDB supply) | 1 | Set |  | 0
B | PDB / AC DB:
i) Incomer -1 No- 100A 4P MCB Isolator.
| ii) Outgoings- 10 nos. -16/20 SP MCB (10KA). | 1 | Set |  | 0
3 | Supply & erection of 230V SPN Wall mounting DB housed in SPN double door DB box consisting of the following:-
A | LDB:
i) Incomer- 1 No- 32A 2P MCB(10KA)
| ii) Outgoing-10 nos. -6A/10A SP MCB(10KA) | 1 | Set |  | 0
B | CDB:
i) 1 no - 25A DP MCB(10KA)
ii) 2 nos. - 10A SP MCB(10KA)
| iii) 6 nos. - 6A SP MCB(10KA) | 1 | Set |  | 0
4 | TIMER D.B. FOR AC IN SERVER RM
i) 1 no - 24 Hours Time switch( Leg rand / Siemens/L&T)
ii) 2 nos. DP contactor, 20A rated( 2 NO)
iii) 2 nos. 16A rated SP MCB (10KA). (For alternative running of 2 nos. 1 Ton AC at 4 Hours interval).
| 2 nos. - Indicating Lamp( Orange & Red/ Blue) | 1 | Set |  | 0
5 | DISTRIBUTION CABLE / WIRE
Supply & lay 1.1 KV grade PVCA CU cable on wall having MS /HDP pipe protection near floor level and clamping as required for the following:-
A) | 25 Sq mm 4 core CU with 2 nos 10 SWG GI wire | 25 | Mtr |  | 0
B) | 16 Sq mm 4 core CU with 2 nos 10 SWG GI wire | 35 | Mtr |  | 0
C) | 10 sq mm 4 core CU with 2 nos 12 SWG GI wire | 40 | Mtr |  | 0
D) | 6 sq mm 4 core CU with 2 nos 12 SWG GI wire | 35 | Mtr |  | 0
E) | 2.5 sq mm 2 core CU for UPS Plate Earthing | 20 | Mtr |  | 0
F) | 4 nos. 16 sq. mm. CU flexible wire through GI flexible pipe complete with end termination | 15 | Mtr |  | 0
with CU sockets.( Meter loop connection with Main SFU & Busbar)
6 | Making end termination of 1.1 KV grade PVCA CU cable with supply of cable end box , brass Gland, CU crimping socket & jointing materials as required for the following:-
A) | 25 Sq mm 4 core CU | 2 | Each |  | 0
B) | 16 Sq mm 4 core CU | 2 | Each |  | 0
C) | 10 sq mm 4 core CU | 6 | Each |  | 0
D) | 6 sq mm 4 core CU | 5 | Each |  | 0
E) | 4 sq mm 2 core CU | 8 | Each |  | 0
7 | Supply draw and connect 1.1 KV grade PVC S/C multistrand CU wire FR grade in suitable PVC conduit & accessories including wall cutting & repairing as required for the following:-
A) | 2X4 + 1X 2.5 sq mm. (Glow sign supply, UPS & LDB DB supply, UPS incoming / outgoing supply).
|  | 200 | Mtr |  | 0
B) | 1X6 SQMM CU wire for earthing | 200 | Mtr |  | 0
C) | 2X2.5 + 1x1.5 sq mm. (for UPS & Raw power Circuit) | 200 | Mtr |  | 0
8 | 16A RAW POWER OUTLET POINT | 3 | Each |  | 0
Wiring for Power outlets from DB with 1.1 KV grade 2x 2.5+1x1.5 PVC insulated copper conductor wire (FR) through suitable size PVC conduit complete with 1 no 6/16A socket with 16A control switch in suitable size modular box with front plates ( Cabtree Legrand), junction box, circular box elbows etc and all other accessories surfaced on wall above false ceiling and concealed by chase cutting on wall & making connection complete. (Maximum 2 nos. sockets cluster in one circuit connecting by looping method).
9 | 16A SOCKET WITH 15A 3Pin Top & 32A Modular SPMCB with SM box & plate | 2 | Each |  | 0
10 | A.C. POWER POINT | 4 | Each |  | 0
A.C. power point wiring from PDB with 1.1KV grade 2 nos. single core 4.0 sq. mm + 1 no. 2.5 sq mm ( Green colour for Earthing) PVC insulated copper conductor wire (FR)through suitable size PVC pipe on wall / ceiling surface with all wiring accessories. The work includes supply & fixing by chase cutting on wall, North West /Cabtree make Starter 18-25A (MS housed) unit with 16A socket & matching 16A Plug top complete with all interconnections for 2T, 1.5 and 1Ton AC.
11 | LIGHT , FAN & RAW POINT :
Supply & wiring with 3x1.5 sq. mm 1.1 KV grade PVC S/C multistrand CU wire (FR) in suitable size PVC conduit & accessories having control board with modular switch mounted on suitable front plate and housed in recessed MS box.
The point wiring also include circuitwiring with 1.1 KV grade 2 nos. single core 2.5 sq. mm +1 no. single core ( green colour for Earth) PVC insulated flexible copper conductor wire through suitable size PVC conduit from DB to Switch board, interconnection and mending good all damages to original finish. (Max.8-10 points or 700- 800Watts per Circuit is allowed).
A | One Light controlled by 6A switch | 20 | Each |  | 0
B | Two Light controlled by 6A switch | 10 | Each |  | 0
C | Bracket fan/Exhaust point with 6A switch | 14 | Each |  | 0
D | Modular type 6A switch, 1 no. 6A 5 pin socket point mounted on suitable front plate on separate switch board other than light / fan switch board. (Power to be tapped from nearest S.B/ LDB). | 11 | Each |  | 0
G | Call bell point with bell push and bell (for manager's Chamber). | 1 | Each |  | 0
12 | UPS POWER OUTLET CLUSTER POINT
Computer socket outlet cluster point wiring with 1.1KV grade 2x 2.5 + 1x1.5 sq. mm. PVC insulated flexible copper conductor wire(FR) through suitable size PVC conduit with all accessories up to connection of 2/3 nos. sockets cluster in one circuit connecting by looping method. The work includes supply and fixing of sockets outlet cluster components as detailed below:-
1 nos.- 16A modular type switch.
3 nos. - 6/16A 5 pin modular type socket
1 each no. - Front plate & MS box.
| ( for Each Table & counters) | 11 | Each |  | 0
13 | TELEPHONE POINT
A | Telephone point wiring with 2 pair PVC insulated CU conductor (0.5mm) telephone wire drawn through PVC conduit. | 3 | Each |  | 0
B | Supply and erection of modular type telephone outlet RJ11 mounted on suitable front plate housed in recessed MS box.
|  | 3 | Each |  | 0
C | Supply and erection of 10 pair telephone terminal box (Krone type housed in MS box).
|  | 1 | Each |  | 0
14 | TELEPHONE CABLE
| Supply, lay and connect PVC insulated CU conductor and armoured 10 pair Telephone cable | 50 | Mtr |  | 0
15 | FAN
Supply, erection and connection of 400 mm 230V oscillating type wall mounted Full metal body bracket Fan with metal back cover.
|  | 9 | Each |  | 0
16 | EXHAUST FAN
| Supply, erection and connection of 225 mm 1400 rpm, 230V Heavy duty exhaust Fan with wire guard net including wall cutting and finishing. | 1 | Each |  | 0
17 | Call Bell
Supply and fixing of call bell with modular type push complete with plate & box to be fixed at the entrance gate.
|  | 1 | Each |  | 0
18 | LIGHT FITTINGS
Supply, erection and connection of fluorescent / compact fluorescent / mini halogen fitting with lamp , ballast / Transformer and other accessories for the following:-
A | PLUTO LHEWEIP6PW1W036 36W 840 2'X2' HAVELLS | 14 | Each |  | 0
B | INTEGRA LHEBGTP5PZ1W015 15W 830 HAVELLS | 15 | Each |  | 0
C | ENDURA LINEAR NEO LHEWEBP5IN1W020 20W 830 | 9 | Each |  | 0
19 | EARTHING
19.1 | Supply and election Earth station with 600 x600x3mm GI Plate with earth strip / wire connecting arrangement including excavation and back filling with 25 mm dia GI pipe for watering.( for UPS Earthing & Light fan Fixtures)
|  | 2 | Each |  | 0
19.2 | Supply and erection of masonry pit for each Earth station having CI/RCC inspection cover. | 2 | Each |  | 0
19.3 | Supply and erection of earth bus on wall ( min. length 0.3 mtr.) on insulator with drilled holes on the bus with GI bolt , nut , washer etc for the following:-
19.4 | With (25x6) mm GI flat | 1 | Each |  | 0
19.5 | With (25x3) mm CU flat | 2 | Each |  | 0
20 | Supply and lay GI flat for earthing underground /on wall including connection for the following:-
| (25x3)mm GI flat | 80 | Mtr |  | 0
21 | COMPUTER LAN SYSTEM :
a) | Supply Laying & connection of CAT-6 wire through 25mm PVC rigid
pipe from HUB to IO box all complete with accessories & 16SWG
| pull out wire for drawing data cable. | 300 | Mts. |  | 0
b) | Providing & fixing I/O Box with RJ 45 socket | 11 | Nos. |  | 0
c) | PATCH CORD 1 MT LENGTH | 11 | Nos. |  | 0
d) | PATCH CORD 2MT LENGTH | 11 | Nos. |  | 0
e) | 24 port Patch Panel | 1 | job
22 | DISMANTLING WORK:
Dismantling of electrical items like light fitings, fan, wires, switches,
| boards etc along with all allied items like LAN and Telephone wires | 1 | job |  | 0
and all items dismantling as per need of the site.
TOTAL COST of ELECTRICAL WORKS (EXCLUDING GST) |  |  |  |  | 0
SGST
CGST
GROSS TOTAL COST (INCLUDING GST) |  |  |  |  | 0
23 | LESS: BUY BACK
Buy Back of all old existing unserviceable WIRES/ DBs/ light fittings/ fans/Switches etc and taking out the same from site (The Contractor should Visit the site & quantify/evaluated properly before quoting the same as salvage value & this value shall be deducted from the Tender Amount.
| NET TOTAL |  |  |  | 0