## Sheet1
TENDER FOR ELECTRICAL WORK OF INDIAN BANK KHAIRAGARH BRANCH (BRANCH + ATM) CHUI KHADAN ROAD, KHAIRAGARH (C.G.)
C | ELECTRICAL WORKS - BRANCH
S. No. | Item/Description |  | Qty | Unit | Rate | Amount
[5 empty] | Rs. | Rs.
A | GENERAL ELECTRICAL WORKS
1 | POINT WIRING:
Providing and fixing, testing and commissioning for po-
int wiring two nos. 1.55 sq. mm/2.5 sq.mm or 4.0 sq.
mm PVC insulated single core stranded copper condu-
ctor wire 1100 volt grade (for Ph&N) and one nos. 1.0
sq. mm/ 1.5 sq. mm PVC insulated single core stand-
ed copper conductor wire 440 volt grade, for earth wire
1.6 mm th. 25 mm dia BEC / NIC / AKG make PVC
conduit pipes. All wires are to be ISI mark approved /
specified make Anchor/ Finolex / Havells complete
with all drops upto boards, stapples, accessories and
hardware etc. Installating the conduit in slabs, wall etc.
The point shall include modular type switches of MK
Anchor, Roma, Crab tree make as approved / specified
in reqiured combination including electronic regulator
, 6 ASP control switch 3-plate ceiling rose, angle or
staight holder adequate size to mount control switches
for lights, fans, call bell, sockets. Sockets for half
points and ceiling fan regulator.
| a) Light / Exhaust Fan points. |  | 64 | nos |  | 0
b) Fan points with regulator (ceiling fastner+ bracket)
| (2x1.50 sq.mm + 1x1.5 sq.mm) |  | 9 | nos |  | 0
| c) Call bell points inclusive of call bell. (BM Cabin) |  | 1 | nos |  | 0
d) 6 Amp 3/5 pin socket half point on Switch Boards
| (2x1.5 sq.mm + 1x1.5 sq.mm) |  | 5 | nos |  | 0
e) 16 Amp 3/5 pin socket half point for BM, Officer
Table & Counters-5 nos and Switch Boards-3 nos
| (2x2.5 sq.mm +1x1.5 sqmm) |  | 5 | nos |  | 0
| f) On/Off starter 25/32 A for AC modular Havell's make. |  | 5 | nos |  | 0
2 | TELEPHONE POINT:
a) Supplying, fixing and testing of telephone socket
point wiring with two line telephone wire of approved
Anchor/Havells/Finolex make in 1.6 mm th 1" dia
PVC conduit pipe including double line tel-Jack
| (modular type) on the switch board. |  | 4 | nos |  | 0
b) Supply and installation of two pair telephone cable
| in PVC pipe of approved make. |  | 80 | m |  | 0
3 | CIRCUIT WIRING:
Supply and installation of circuit in app. make 1.6 mm
thick, 25mm dia PVC pipes and at places where deco-
rum is to be maintained in PVC casings with approved
make PVC insulated multistraind copper wire as under
The rate shall beinclusive of all necessary fittings like
junction boxes, tees, bends, saddles screws etc
complete. PVC pipe to be of BEC/NIC/AKG make and
wire of Havells, Anchor, Finolex make.
| a) 4x2.5 sq.mm + 2x1.5 sq.mm for Computer/ UPS |  | 90 | mts |  | 0
| b) 2x2.5 sq.mm + 1x1.5 sq.mm for Lighting Boards |  | 70 | mts |  | 0
| c) 2x4 sq.mm + 1x2.5 sq.mm for AC power supply |  | 75 | mts |  | 0
| d) 4x10 sq.mm + 1x6.0 sq.mm for Main Panel / UPS |  | 25 | mts |  | 0
4 | EARTHING:
Providing, fixing, testing and commisioning copper ea-
rth plate2x 600x600x 3mm including accessories and
providing enclosure in CM, cover plate having locking
arrangement and watering pipe 20mm GI "B" class etc
| with salt, charcoal, earthing electrode complete. |  | 2 | nos |  | 0
5 | EARTHING WIRING:
Supplying and installation of 1x6 sq.mm specified /
approved make flexible copper PVC insulated earthing
wire through 20 mm dia B class G.I. pipe burried not
less than 2' below ground level. The wire shall be with-
out joint except connection with bolted link. The rate
shall include for all earthing connections on the main
panel with the earth station by means of brass nuts
and bolts using socket terminals.
| PVC conduit to be of BEC, NIC, AKG make. |  | 50 | mts |  | 0
6 | COMPUTER UPS POINT:
Supply and installation and connection of modular type
app./ specified switch and socket complete with PVC
box plate screws and all other accessories.
| a) 3 Nos. socket + 1 Nos. switches (6A) + indicator |  | 9 | nos |  | 0
| b) 1 Nos. socket + 1 Nos. switch (6/16A) |  | 9 | nos |  | 0
7 | MAIN PANEL:
Supply, installation, testing and commissioning of the
following items on the main panel:
| 1) 100 amps cut outs 3 nos. on the panel. |  | 3 | nos |  | 0
2) Main switch with HRC fuses, 100 amps. Crompton
| Greaves, L&T or Havell's make. |  | 1 | nos |  | 0
3) MCB DB having incomer 1 nos.63 amps TPN MCB
incoming and 4 nos. 32 A TPN & 4 nos 32 A SP
MCB outgoing for AC. (Havell's/MDS make factory
| fabricated). |  | 1 | nos |  | 0
4) TPN MCB 63 amps, 415 V with enclosure (Havell's/
| MDS make) |  | 1 | nos |  | 0
5) Supply, installation, testing and commissioning of
distribution board incoming 32 TPN MCB - 1 Nos.
outgoing 6/10 Amp SPMCB - 8 Nos. and 1 Nos.40A
| DPMCB for Lighting. |  | 2 | nos |  | 0
6) MCB DB having incomer 2 nos. 40 A DP MCB and
10 nos. 10/16 A.SPMCB for UPS power points.
| (Havell's/MDS make factory fabricated) |  | 1 | nos |  | 0
| 7) 3 phase indicator lamp with gang box. |  | 1 | nos |  | 0
8 | MAIN POWER CABLE:
Supply and installation of 4 x 35 sq.mm Aluminium
armoured cable with accessories required for its fitting
in position, for power supply from CSEB pole and DG
| set. Cable should be of CCI/GLOSTER/FINOLEX make |  | 50 | mtr |  | 0
9 | ATM POWER SUPPLY:
a) Supply and installation of 4 x 16 sq.mm Aluminium
armoured cable with accessories required for its
fitting in position, for power supply from Main Panel
| to ATM Cable should be of CCI/GLOSTER/FINOLEX |  | 20 | mtr |  | 0
make.
10 | CEILING FAN:
Supplying ,erecting,and testing of approved/specified
make Crompton, Havel, Orient electric ceiling fans
complete with down rod, canopy, blades and speed
regulator 230-250 volts including connection with all
| necessary materials as required. |  | 9 | nos |  | 0
11 | WALL FAN:
Supplying, erecting and testing of approved / specified
Havels, Oreint or Crompton make oscillating cabin fan
complete with base, blades, gaurds, speed regulators
etc. 230-250 volts with connections,raw bolts/anchor
| hole fastener completely finished as required. |  | 2 | nos |  | 0
12 | EXHAUST FAN:
Supplying, erecting of Crompton/Havells/Usha make
trans air exhaust fan complete with motor, mounting
frame, blades with connection, bolts, anchor fasteners
| etc complete as required. |  | 2 | nos |  | 0
13 | LIGHT FIXTURES:
Supplying, fixing and testing of approved Phillips
Havells, Wipro, Crompton, Syska or its equiv
light fittings complete in all respect
1. Recessed mounting LED Panel 35 w Phillips,
| Crompton, Wipro or its equiv 24"x24" |  | 18 | Nos |  | 0
2. Recessed mounting LED Down Light 12w make
| Phillips, Wipro, Crompton, Syska or its equiv |  | 22 | Nos
3. Supply and installation LED Batten Light 18 w
| make Phillips, Wipro, Crompton or its equivalent |  | 6 | Nos |  | 0
14 | DATA CABLING FOR COMPUTERS:
a) Providing, supplying and laying of new D-Link conce
aled/open data line Cat 6e in separate ISI pvc casing
caping (as and where required) for the lcation of com
puter terminals, inclusive of fixing of jack socket of
link or equivalent make including testing, commissio
| ning, certification etc. complete. |  | 290 | mtr |  | 0
b) Supplying and installation of jack type computer so-
cket Link make RJ-45, complete with female unit on
counters/side table/ walls along with other electrical
| output. |  | 10 | nos |  | 0
c) Providing and fixing
| i) D-link Patch cord Cat-6 2 metre B/Y Color |  | 10 | nos |  | 0
| ii) D-link Patch cord Cat-6 1 metre B/Y Color |  | 10 | nos |  | 0
| TOTAL |  |  |  | Rs. | 0
D | ELECTRICAL WORKS - ATM
Sr. No. | Element | Specifications | Qty | Unit | Rate (Rs.) | Amount (Rs.)
1 | UPS Cabling | UPS Cabling of 2.5 Sq.mm Finolex Fire Guard Cable with conduiting | 1 | L.S. |  | 0
2 | Power Cabling | Raw Power Cabling of 4.0 sq.mm Finolex Fireguard Cable with conduiting for AC and power points. | 2 | L.S. |  | 0
3 | Signage Cabling | Signage cabling of 2.5 sq.mm Finolex Fireguard Cable with conduiting | 1 | L.S. |  | 0
4 | Earthing cable | 6 Sq.mm copper wire with flexi conduit | 1 | L.S. |  | 0
5 | Lighting Cabling | Lighting Cabling of 1.0 sq.mm or 3/22 Finolex fire guard cable with conduiting | 1 | L.S. |  | 0
6 | Distribution Board
a |  | Incoming supply MCB TPN 32 A | 1 | nos |  | 0
b |  | UPS outgoing supply MCB DP 32A | 1 | nos |  | 0
c |  | UPS incoming supply MCB DP 32A | 1 | nos |  | 0
d |  | A/c Supply MCB SPN 25A | 1 | nos |  | 0
e |  | Timer AC 20~25 A (Crab Tree / GIC) | 1 | nos |  | 0
f |  | Timer for Glow Sign board 20~25 A (Crab Tree /GIC) | 1 | nos |  | 0
g |  | Light points | 4 | nos |  | 0
h |  | 2 Switch + 2 Socket | 2 | nos |  | 0
i |  | A/c point 32 A DP switch | 1 | nos |  | 0
j |  | Light MCB SP 10 A | 4 | nos |  | 0
7 | LED Panel Light | Providing and fixing of LED panel 36 w of Wipro Havells Crompton make. | 1 | nos. |  | 0
8 | LED Down Light | 12 W LED spot light of Wipro Crompton Havels make | 2 | nos. |  | 0
9 | Mains cabling | 4 core -16 sq.mm copper armoured cable of ISI make from Distribution board to ATM room. | 5 | m |  | 0
10 | I/O Box | Providing and fixing of RJ-45 I/O box | 2 | nos. |  | 0
11 | LED Batten light | 1x40 w LED batten light in back room | 1 | nos. |  | 0
12 | Data cabling works | Providing and laying of Cat 6-e D-Link make data cable from Router to the ATM room | 50 | m |  | 0
| Total |  |  |  | Rs. | 0
| TOTAL OF ELECTRICAL WORKS (C + D) |  |  |  | Rs. | 0
| Add GST @ 18% |  |  |  | Rs. | 0
| FINAL AMOUNT |  |  |  | Rs. | 0
| Date: |  | Seal & Signature of the contractor
Place: